H & W Integrated Control System

Hardware Specification

Version 2.0  —  Two Elegoo Mega 2560 controllers

# 1. Architecture Overview

Two Elegoo Mega 2560 controllers (ATmega2560, 16MHz, 54 digital I/O, 16 analogue inputs). Both powered from the 15VDC battery bus. Communication over RS485 at 9600 baud via spare 1mm T&E cable. All data logging at H via SD card, with W transmitting readings to H every 250ms.

| Item | W (Workshop) | H (House) |
| --- | --- | --- |
| Controller | Elegoo Mega 2560 | Elegoo Mega 2560 |
| Power input | 15VDC battery bus via barrel jack | 15VDC battery bus via barrel jack |
| Temp sensors | 6 × DS18B20 (1-Wire bus) | 6 × DS18B20 (1-Wire bus) |
| RS485 links | 2 × MAX485 (Growatt Modbus + H link) | 1 × MAX485 (W link) |
| 230VAC switching | 8-ch relay board (5 loads, 3 spare) | SSR-40DA zero-crossing only (heater) |
| 15VDC switching | 8-ch relay board (8 loads, 0 spare) | 8-ch relay board (7 loads, 1 spare) |
| Additional relay board | 4-ch board (vac isolation valve 2ch + buzzer signal 1ch + spare 1ch) | Not required |
| Display | — | 3.5″ ILI9488 TFT 480×320 SPI |
| SD card | — | MicroSD SPI module |
| RTC | — | DS3231 I2C |
| Current sensing | INA219 I2C (solar pump) | — |
| Voltage sensing | — | Resistor divider on ADC A0 (15V bus) |
| Grid detection | — | AC zero-crossing detector on INT0 (D2) |
| Heater control | — | SSR-40DA driven from D27 (digital output) |

# 2. Bill of Materials

All prices approximate UK retail. Buy from reputable sellers.

## 2.1 Controllers

| Item | Qty | Unit | Notes |
| --- | --- | --- | --- |
| Elegoo Mega 2560 R3 | 2 | ~£12 | CH340 USB chip — install CH340 driver on PC once |

## 2.2 Temperature Sensors

| Item | Qty | Unit | Notes |
| --- | --- | --- | --- |
| DS18B20 waterproof probe (1m cable) | 12 | ~£2 | 12 sensors total (6 at W, 6 at H). 1-Wire bus, individually addressable. Full 3-wire connection only. Discard readings of 85.00°C, -127°C, -128°C. |
| 4.7kΩ resistor | 2 | Pence | One pull-up per 1-Wire bus (W bus, H bus) |

## 2.3 RS485 & Communications

| Item | Qty | Unit | Notes |
| --- | --- | --- | --- |
| MAX485 RS485 module (5V) | 3 | ~£1 | 2 × at W (Growatt Modbus + H link), 1 × at H (W link) |
| 120Ω termination resistor | 4 | Pence | One at each end of each RS485 run (2 runs = 4 resistors) |
| 560Ω resistors for line bias | 2 sets | Pence | One set per RS485 run: 560Ω pull-up on A line, 560Ω pull-down on B line. Check if MAX485 boards include internally before adding. |

## 2.4 Relay Boards & Switching

| Item | Qty | Unit | Notes |
| --- | --- | --- | --- |
| 8-channel 5V optocoupled relay board | 3 | ~£6 | W 230VAC board, W 15VDC board, H 15VDC board. Verify boards include flyback diodes on relay coils. If not, add 1N4007 across each coil. |
| 4-channel 5V optocoupled relay board | 1 | ~£3 | W: vacuum isolation valve pair (2ch) + buzzer signal to H (1ch) + spare (1ch) |
| SSR-40DA zero-crossing solid state relay | 1 | ~£6 | At H only — heater cycle-burst control. Zero-crossing type. 40A rating gives thermal headroom at 12.5A load. |
| Heatsink for SSR | 1 | ~£2 | Mount SSR externally on H enclosure. Required. |
| IRLZ44N logic-level N-channel MOSFET | 1 | ~£1 | At W — solar pump 15VDC switching. Fully enhanced at 5V gate drive. |
| 120Ω gate resistor (for MOSFET) | 1 | Pence | Series resistor on Mega PWM pin to MOSFET gate. Same value as RS485 termination resistors — no extra component needed. |
| 1N4007 flyback diode (solar pump) | 1 | Pence | Across solar pump terminals to absorb back-EMF |

## 2.5 Display, Storage & RTC (H only)

| Item | Qty | Unit | Notes |
| --- | --- | --- | --- |
| 3.5″ TFT LCD ILI9488 SPI module | 1 | ~£16 | 480×320, SPI. Verify ILI9488 driver chip on listing. |
| MicroSD SPI module | 1 | ~£2 | Shares SPI bus with display. Separate CS pin. |
| MicroSD card 16GB (FAT32) | 1 | ~£5 | Years of logging capacity at 250ms interval |
| DS3231 RTC module (I2C) | 1 | ~£2 | Essential for 5am heating trigger and time-gated security alerts. I2C address 0x57/0x68. |
| Panel-mount momentary button 12mm | 3 | ~£1 | SELECT, UP (▲), DOWN (▼) at H display. RESET removed — now a display menu item on page 4. |

## 2.6 Sensing & Monitoring

| Item | Qty | Unit | Notes |
| --- | --- | --- | --- |
| INA219 current sensor module (I2C) | 1 | ~£2 | At W: solar pump current monitoring. I2C address 0x40. Wire in series with pump positive feed. |
| AC zero-crossing detector module | 1 | ~£2 | At H: wired to INT0 (D2). Fires interrupt every 20ms on grid present. Grid outage = no interrupt >50ms. Used for SSR cycle timing. |
| BES fan speed controller (ref 27219) | 1 | ~£52 | S&P HCBB/4-450/H compatible. Manual dial speed control. Wired in line with fan. Relay controls on/off. |
| 12V DC-DC buck converter module (min 1A) | 1 | ~£3 | Steps down 15VDC bus to 12VDC for PC fans. Mount inside W enclosure. |
| IRLZ44N MOSFET (PC fan speed control) | 1 | ~£1 | At W: PC fan 12VDC PWM switching at 25kHz. Separate from solar pump MOSFET. |
| 10kΩ resistors (fan tachometer pull-up) | 2 | Pence | One per fan tachometer wire (pin 3). Pull-up to 5V. Safe directly on Mega input pin. |

## 2.7 Voltage Dividers

| Signal | Location | Resistors | Output at 12V | Output at 15V | Notes |
| --- | --- | --- | --- | --- | --- |
| PIR sensor output | W — D2 | 10kΩ + 4.7kΩ | 3.50V ✓ | 4.80V ✓ | 15VDC output |
| Unlock button (1mm T&E live) | W — D10 | 10kΩ + 4.7kΩ | 3.50V ✓ | 4.80V ✓ | 15VDC bus |
| Outside light button (1mm T&E) | W — D11 | 10kΩ + 4.7kΩ | 3.50V ✓ | 4.80V ✓ | 15VDC bus |
| Log burner temp module | H — D3 | 10kΩ + 5.6kΩ | 4.37V ✓ | 5.45V ⚠ | 12VDC output. Use 10k+5.6k only if bus will not exceed 13V. |
| 15V bus voltage monitor | H — A0 | 10kΩ + 4.7kΩ | 3.50V ✓ | 4.80V ✓ | Scales bus voltage to ADC range |

Note: Vacuum sensor (D9 at W), door reed switch, door handle reed switch, window winch reed switches, safety limit switch, summer/winter switch, manual relock switch, boost button, alert reset, display cycle buttons are all dry contacts with Mega pull-up — no voltage divider needed.

## 2.8 Power Supply Components

| Item | Qty | Unit | Notes |
| --- | --- | --- | --- |
| 1N4007 diode (reverse polarity protection) | 2 | Pence | One per controller on 15VDC feed to barrel jack |
| 100µF electrolytic capacitor | 2 | Pence | Decoupling on controller power rail |
| Fuse holder + 1A fuse | 2 | ~£1 | Inline fuse on 15VDC feed to each controller |
| 12VDC backup PSU | 1 | TBD | At H. Switched by relay on H 15VDC board. Activates when bus drops below 12V. |

## 2.9 Enclosures & Miscellaneous

| Item | Qty | Unit | Notes |
| --- | --- | --- | --- |
| Plastic project box ~200×150×80mm | 2 | ~£6 | One per controller. Cut-outs for display, terminals, USB, ventilation slots. |
| Screw terminal blocks (3.5mm pitch) | Assorted | ~£5 | For all external wire connections into enclosures |
| DuPont jumper wires / header pins | Assorted | ~£3 | Internal connections between Mega and modules |
| Heat shrink + cable ties | Assorted | ~£3 | Cable management and insulation |
| Ferrite cores | 4 | ~£1 | Two per RS485 cable end to suppress interference from adjacent 230VAC cables |

Estimated total BOM cost (excluding sensors and actuators already purchased): £75–£95

# 3. Wiring Architecture

## 3.1 Power Supply

- Both Mega controllers powered from 15VDC battery bus via: inline 1A fuse → 1N4007 reverse-polarity diode → barrel jack (centre positive, 2.1mm)

- Alternatively: wire directly to Mega VIN and GND pins via screw terminals (same 7–20V range, no barrel jack connector to work loose)

- Mega onboard regulator provides 5V and 3.3V for all modules and sensors

- 15VDC relay contact loads (valves, lock, alarm, buzzer signal etc.) fed directly from 15VDC bus through relay contacts

- 5V relay board coils powered from Mega 5V pin

- ⚠ Never connect 15VDC directly to Mega 5V pin — use barrel jack or VIN pin only

## 3.2 Inter-Controller RS485 Link (H ↔ W)

- Runs over spare 1mm T&E cable between H and W (40m)

- MAX485 at each end. Connect: A to A, B to B, GND to GND (use earth conductor for GND)

- 120Ω termination resistor across A–B at both ends

- Line bias: 560Ω pull-up on A to 5V, 560Ω pull-down on B to GND — at one end only. Check if MAX485 boards include internally.

- Baud: 9600. Poll interval: 250ms. W→H and H→W packets exchanged every 250ms.

- MAX485 DE/RE pins tied together, driven from one Mega digital pin (HIGH = transmit, LOW = receive)

## 3.3 Growatt Modbus RS485 (at W)

- Separate MAX485 module — do not share with inter-controller link

- Connects to existing RS485 screened cable to Growatt inverter

- Baud: 9600. Poll interval: 850ms (Growatt manufacturer minimum)

- Reads: PV string 1 & 2 (V, A, kW), total PV kW, grid import/export kW, grid voltage, grid frequency, battery SOC %, battery charge/discharge kW, battery voltage, load power kW, inverter temp, inverter status code, fault codes, today's PV generation kWh

- Verify register addresses and export/import sign convention during commissioning before enabling heater control

## 3.4 DS18B20 1-Wire Buses

- W bus (D13 at W): 6 sensors — solar hot, solar cold, UFH supply (at pump/return, 28°C pump-off check), UFH post TMV (after TMV, 45°C hard lockout), Workshop air, outside air. 4.7kΩ pull-up to 5V.

- H bus (D13 at H): 6 sensors — tank bottom, tank middle, tank top, hot pipe, cold pipe, heater output. 4.7kΩ pull-up to 5V.

- Each DS18B20 has unique 64-bit address. Scan all sensors during commissioning, map to physical locations, store as firmware constants.

- Use full 3-wire connection (VDD, GND, Data) — parasitic power mode not recommended for reliability

- Plan physical routing to keep bus runs as short as possible. Max reliable 1-Wire run ~100m with good cable.

## 3.5 Valve & Lock Wiring

Two wiring types are used depending on valve type:

Type A — H-bridge (H tank valves, vacuum isolation valve, door lock):

- Relay 1 COM → Device terminal A | Relay 2 COM → Device terminal B

- Both relay NO → +15VDC | Both relay NC → GND

- Relay 1 ON, Relay 2 OFF: terminal A = +15V, terminal B = GND — opens/unlocks

- Relay 1 OFF, Relay 2 ON: terminal A = GND, terminal B = +15V — closes/locks

- Both OFF: both terminals at GND — holds position, no power drawn

- Pulse: 7 seconds for valves, 1 second for door lock. Both relays OFF after pulse.

- Interrupt: new command mid-pulse → 200ms dead-time → new command for full pulse duration

Type B — Direction + Power relay (W UFH cold valve, W solar cold valve):

- These valves have a permanently connected GND and two +15VDC wires (Wire A = open, Wire B = close)

- Direction relay: COM → power relay NO output. NO → Wire A. NC → Wire B.

- Power relay: COM → +15VDC. NO → direction relay COM. NC → nothing.

- To open: set direction relay ON, then energise power relay → +15V flows to Wire A

- To close: set direction relay OFF, then energise power relay → +15V flows to Wire B via NC

- To hold: de-energise power relay → valve holds position, no power drawn

- No timed pulse — power until end stop reached. Built-in end-stop protection — motor stalls safely.

- Cut power relay after movement complete.

- ⚠ Type A valves: implement 200ms dead-time between relay direction changes. Type B valves: always cut power relay before changing direction relay.

## 3.6 Solar Pump Control (at W)

- Solar pump is 2-wire 12/15VDC brushless, under 10W. No separate PWM signal wire.

- Speed controlled by MOSFET (IRLZ44N) switching 15VDC supply at clocking rate

- Mega PWM pin → 120Ω gate resistor → IRLZ44N gate. Source to GND, drain to pump negative. Pump positive to 15VDC bus.

- 1N4007 flyback diode across pump terminals (anode to negative, cathode to positive) to absorb back-EMF

- INA219 current sensor wired in series with pump positive feed. I2C to Mega (SDA=D20, SCL=D21).

- Minimum ON pulse: 200ms. Current sampled during ON period only, after 50ms spin-up. Calibrate minimum current threshold during commissioning.

## 3.7 PC Fan Control (at W)

- 2 × Fractal Design Dynamic X2 GP-14 (3-pin, 12VDC). Both fans share same PWM signal and run at same speed.

- 12V DC-DC buck converter steps down 15VDC bus to 12VDC for fan supply (pin 2 of each fan)

- Fan GND (pin 1) connected to MOSFET (separate IRLZ44N from solar pump) drain. MOSFET source to GND.

- Mega D45 PWM → 120Ω gate resistor → IRLZ44N gate. 25kHz PWM frequency for smooth 3-pin fan speed control.

- Fan tachometer (pin 3): open collector. 10kΩ pull-up to 5V on each fan separately. Safe directly on Mega input pins D41 and D42.

- Fan 1 tachometer → D41. Fan 2 tachometer → D42.

- Momentary push button at W door → D43 (pull-up enabled) — press sets 8-hour full speed timer

- 3kW heater switched by SSR-40DA zero-crossing solid state relay. Mount SSR on heatsink externally on H enclosure.

- SSR control input wired to Mega D27 (digital output, not PWM). 5V signal is within SSR control range (3–32VDC).

- Heater control method: cycle-burst. Mega toggles D27 ON/OFF at each zero-crossing interrupt (every 20ms at 50Hz). Outer control loop updates ON-cycle ratio every 850ms from Growatt export/import data.

- Zero-crossing detector module wired to Mega INT0 (D2) at H. Fires interrupt every 20ms when grid present.

- Grid outage detection: if >50ms without zero-crossing interrupt → grid is down. Heater forced off. Logged immediately.

- Grid restore: interrupts resume → logged, heater control resumes.

- ⚠ All 230VAC wiring must be installed and verified by a competent person. Ensure correct fusing and isolation.

- ⚠ SSR carries up to 12.5A at 3kW. Use 4mm² cable, rated fuse, and confirmed adequate heatsink.

- ⚠ Confirm SSR purchased is zero-crossing type (SSR-40DA).

## 3.8 Voltage Monitoring (at H)

- Resistor divider: 10kΩ top + 4.7kΩ bottom across 15VDC bus at H

- Divider midpoint to H Mega A0. At 15V: output = 4.80V. At 12V: output = 3.84V. Both within 5V ADC range.

- Calibrate during commissioning: measure actual bus voltage with multimeter, compare to ADC reading, apply correction factor in firmware if needed.

## 3.9 SPI Bus at H (display + SD card)

- ILI9488 display and MicroSD module share SPI bus (MOSI=D51, MISO=D50, SCK=D52)

- Display CS: D53. SD card CS: D48. Display DC: D49. Display RST: D47 (or tie to Mega RESET).

- Only one device active at a time via CS pins.

## 3.10 I2C Bus at H (RTC)

- DS3231 RTC: SDA=D20, SCL=D21. Address 0x57/0x68.

- No I2C devices at W (INA219 is on W I2C bus: SDA=D20, SCL=D21, address 0x40).

## 3.11 Enclosure Notes

- Passive ventilation slots required in both enclosures — relay boards and Mega generate heat in enclosed space

- SSR heatsink must be mounted externally on H enclosure — do not enclose inside plastic box

- Ferrite cores on RS485 cables at each end to suppress 230VAC interference

- Label all terminals clearly during installation

- All low-voltage (5V, 15VDC) wiring routed and separated from 230VAC wiring inside enclosures

# 4. Pin Assignments

Type colour coding: Digital Input (green), Digital Output (navy), Analogue Input (brown), PWM (purple), UART/RS485 (blue), SPI/I2C/1-Wire (dark green)

## 4.1 W Controller — Digital Inputs

| Pin | Signal | Type | Notes |
| --- | --- | --- | --- |
| D2 (INT0) | PIR sensor output | Digital Input | 15VDC output — 10kΩ + 4.7kΩ divider required. Use INT0 for fast response. |
| D3 (INT1) | Door handle reed switch | Digital Input | Dry contact. Pull-up enabled. Closed when handle pushed. |
| D4 | Door reed switch | Digital Input | Dry contact. Pull-up enabled. Closes when door OPENS, opens when door CLOSED. |
| D5 | Winch reed: fully open | Digital Input | Dry contact. Pull-up enabled. |
| D6 | Winch reed: fully closed | Digital Input | Dry contact. Pull-up enabled. |
| D7 | Winch reed: manual lock | Digital Input | Dry contact. Pull-up enabled. |
| D8 | Window winch safety limit switch | Digital Input | Dry contact, normally open. Pull-up enabled. Closes at over-open limit. |
| D9 | Vacuum sensor | Digital Input | Dry contact. Pull-up enabled. HIGH (open) = low vacuum. LOW (closed) = full vacuum. |
| D10 | Unlock button signal (1mm T&E live) | Digital Input | 15VDC bus — 10kΩ + 4.7kΩ divider required. |
| D11 | Outside light button signal (1mm T&E) | Digital Input | 15VDC bus — 10kΩ + 4.7kΩ divider required. |
| D12 | Manual relock suppression switch | Digital Input | Dry contact. Pull-up enabled. HIGH = suppression ON (no relock). |
| D13 | DS18B20 1-Wire bus (W — 6 sensors) | Digital (1-Wire) | 4.7kΩ pull-up to 5V. See 1-Wire section for sensor list. |
| D41 | PC fan 1 tachometer input | Digital Input | Open collector. 10kΩ pull-up to 5V. 2 pulses/revolution. Safe directly on Mega pin. |
| D42 | PC fan 2 tachometer input | Digital Input | Open collector. 10kΩ pull-up to 5V. 2 pulses/revolution. Safe directly on Mega pin. |
| D43 | Fan full speed timer button (momentary) | Digital Input | Dry contact. Pull-up enabled. Press = sets 8-hour full speed timer. |

## 4.2 W Controller — Digital Outputs

| Pin | Signal | Type | Notes |
| --- | --- | --- | --- |
| D22 | UFH cold valve — direction relay (SPDT) | Digital Output | 15VDC relay board ch1. COM to valve. NO = Wire A (open). NC = Wire B (close). GND permanent. No power relay. |
| D23 | Spare | Digital Output | Previously UFH cold power relay — removed. Auto-cutout eliminates need. |
| D24 | Solar cold valve — direction relay (SPDT) | Digital Output | 15VDC relay board ch3. COM to valve. NO = Wire A (open). NC = Wire B (close). GND permanent. |
| D25 | Spare | Digital Output | Previously solar cold power relay — removed. Auto-cutout eliminates need. |
| D26 | UFH 230VAC pump | Digital Output | 230VAC relay board ch1. |
| D27 | 230VAC wall fan on/off | Digital Output | 230VAC relay board ch2. Fan speed set manually via BES controller. |
| D28 | Fan flap 15VDC actuator | Digital Output | 15VDC relay board ch5. Open before fan ON, close after fan OFF. |
| D29 | Electric door lock relay 1 | Digital Output | 15VDC relay board ch6. H-bridge pair with D39. Pulse 1s. |
| D30 | 230VAC external LED lights | Digital Output | 230VAC relay board ch3. |
| D31 | Window winch — direction open | Digital Output | 230VAC relay board ch4. Energise simultaneously with D32 only. Never with D33. |
| D32 | Window winch — power | Digital Output | 230VAC relay board ch6. Energise simultaneously with D31 or D33 only. Never ON alone. |
| D33 | Window winch — direction close | Digital Output | 230VAC relay board ch5. Energise simultaneously with D32 only. Never with D31. |
| D34 | 1mm T&E live (mid-point LED) | Digital Output | Direct output. Steady HIGH = unlocked. 1s/1s = fault. 1s ON/5s OFF = manual heater active (no fault). |
| D35 | RS485 DE/RE — inter-controller link | Digital Output | HIGH = transmit, LOW = receive. |
| D36 | RS485 DE/RE — Growatt Modbus | Digital Output | HIGH = transmit, LOW = receive. |
| D37 | Vacuum isolation valve — OPEN relay | Digital Output | 4-ch relay board ch1. H-bridge pair with D38. |
| D38 | Vacuum isolation valve — CLOSE relay | Digital Output | 4-ch relay board ch2. H-bridge pair with D37. |
| D39 | Electric door lock relay 2 | Digital Output | 15VDC relay board ch8. H-bridge pair with D29. |
| D40 | Buzzer signal to H (2.5mm T&E earth) | Digital Output | 4-ch relay board ch3. |
| D41 | 230VAC vacuum pump | Digital Output | 230VAC relay board ch7. |
| D42 | 15VDC alarm sounder | Digital Output | 15VDC relay board ch7. Sounds 1 min on intrusion, then auto-stops. |

## 4.3 W Controller — PWM Output

| Pin | Signal | Type | Notes |
| --- | --- | --- | --- |
| D44 | Solar pump speed (clocking PWM) | PWM Output | Timer5. To IRLZ44N gate via 120Ω resistor. Clocking rate not high-frequency PWM. |
| D45 | PC fan speed (25kHz PWM) | PWM Output | Timer5. To separate IRLZ44N gate via 120Ω resistor. Both fans share same PWM signal. 25kHz for smooth 3-pin fan speed control. |

## 4.4 W Controller — UART / RS485

| Pin | Signal | Type | Notes |
| --- | --- | --- | --- |
| TX1 (D18) | RS485 TX — inter-controller link | UART1 / RS485 | To MAX485 DI pin. |
| RX1 (D19) | RS485 RX — inter-controller link | UART1 / RS485 | From MAX485 RO pin. |
| TX2 (D16) | RS485 TX — Growatt Modbus | UART2 / RS485 | To MAX485 DI pin. |
| RX2 (D17) | RS485 RX — Growatt Modbus | UART2 / RS485 | From MAX485 RO pin. |

## 4.5 W Controller — I2C & 1-Wire

| Pin | Signal | Type | Notes |
| --- | --- | --- | --- |
| SDA (D20) | INA219 current sensor SDA | I2C | Address 0x40. Solar pump current monitoring. |
| SCL (D21) | INA219 current sensor SCL | I2C |  |
| D13 | DS18B20 1-Wire bus (W — 6 sensors) | Digital (1-Wire) | 4.7kΩ pull-up to 5V. Sensors: solar hot, solar cold, UFH supply (at pump), UFH post TMV (45°C lockout), Workshop air, outside air. |

## 4.6 W Controller — Analogue Inputs

| Pin | Signal | Type | Notes |
| --- | --- | --- | --- |
| A0 | Spare | Analogue Input | Previously fan potentiometer — removed. Available for future use. |

## 4.7 H Controller — Digital Inputs

| Pin | Signal | Type | Notes |
| --- | --- | --- | --- |
| D2 (INT0) | AC zero-crossing detector | Digital Input | Module output 3.3–5V — safe direct connection. Fires every 20ms on grid present. >50ms gap = grid outage. |
| D3 (INT1) | Log burner 12VDC temp module | Digital Input | 12VDC output — 10kΩ + 5.6kΩ divider required. HIGH when jacket > 28°C. |
| D4 | SELECT button | Digital Input | Dry contact. Pull-up enabled. Panel-mount momentary. Enters item mode / confirms selection / exits item mode at boundary. |
| D5 | UP (▲) button | Digital Input | Dry contact. Pull-up enabled. Panel-mount momentary. Scrolls pages (page mode) or items (item mode) or decrements value (option mode). |
| D6 | DOWN (▼) button | Digital Input | Dry contact. Pull-up enabled. Panel-mount momentary. Scrolls pages (page mode) or items (item mode) or increments value (option mode). |
| D7 | Spare | Digital Input | Previously RESET button — removed from design. Available for future use. |

## 4.8 H Controller — Digital Outputs

| Pin | Signal | Type | Notes |
| --- | --- | --- | --- |
| D22 | Log burner cold valve — OPEN | Digital Output | 8-ch relay board ch1. H-bridge pair with D23. |
| D23 | Log burner cold valve — CLOSE | Digital Output | 8-ch relay board ch2. H-bridge pair with D22. |
| D24 | Bottom-of-tank valve — OPEN | Digital Output | 8-ch relay board ch3. H-bridge pair with D25. |
| D25 | Bottom-of-tank valve — CLOSE | Digital Output | 8-ch relay board ch4. H-bridge pair with D24. |
| D26 | 2-port valve — OPEN (heater side) | Digital Output | 8-ch relay board ch5. H-bridge pair with D28. COM to valve terminal A. |
| D27 | Heater SSR control | Digital Output | Direct output to SSR-40DA control input. NOT through relay board. Toggled cycle-by-cycle via zero-crossing interrupt. |
| D28 | 2-port valve — CLOSE (mid-tank side) | Digital Output | 8-ch relay board ch6. H-bridge pair with D26. COM to valve terminal B. |
| D29 | 12VDC backup PSU relay | Digital Output | 8-ch relay board ch7. Energise when bus < 12V. De-energise above 12.5V. |
| D30 | RS485 DE/RE — inter-controller link | Digital Output | HIGH = transmit, LOW = receive. |
| D31 | Spare | Digital Output | Previously boost LED — removed from design. Available for future use. |
| D32 | Display backlight PWM | Digital Output | PWM to TFT backlight. Dims/off on inactivity. Full on fault active. |

## 4.9 H Controller — UART / RS485

| Pin | Signal | Type | Notes |
| --- | --- | --- | --- |
| TX1 (D18) | RS485 TX — inter-controller link | UART1 / RS485 | To MAX485 DI pin. |
| RX1 (D19) | RS485 RX — inter-controller link | UART1 / RS485 | From MAX485 RO pin. |

## 4.10 H Controller — SPI Bus (display + SD)

| Pin | Signal | Type | Notes |
| --- | --- | --- | --- |
| D51 (MOSI) | SPI MOSI — display + SD | SPI | Shared bus. |
| D50 (MISO) | SPI MISO — display + SD | SPI | Shared bus. |
| D52 (SCK) | SPI SCK — display + SD | SPI | Shared bus. |
| D53 | Display CS (ILI9488) | SPI | Active LOW. |
| D49 | Display DC (data/command) | SPI |  |
| D47 | Display RST | SPI | Or tie to Mega RESET pin. |
| D48 | SD card CS | SPI | Active LOW. |

## 4.11 H Controller — I2C & 1-Wire

| Pin | Signal | Type | Notes |
| --- | --- | --- | --- |
| SDA (D20) | DS3231 RTC SDA | I2C | Address 0x57/0x68. |
| SCL (D21) | DS3231 RTC SCL | I2C |  |
| D13 | DS18B20 1-Wire bus (H — 6 sensors) | Digital (1-Wire) | 4.7kΩ pull-up to 5V. Sensors: tank bottom, tank middle, tank top, hot pipe, cold pipe, heater output. |

## 4.12 H Controller — Analogue Inputs

| Pin | Signal | Type | Notes |
| --- | --- | --- | --- |
| A0 | 15VDC bus voltage monitor | Analogue Input | Resistor divider: 10kΩ + 4.7kΩ. 15V → 4.80V. 12V → 3.84V. |

# 5. Relay Board Channel Allocation

## 5.1 W — 230VAC Relay Board (8-channel)

| Channel | Load | Status | Notes |
| --- | --- | --- | --- |
| ch1 | UFH 230VAC pump | Used |  |
| ch2 | 230VAC wall fan (via BES speed controller) | Used | On/off only. Speed set manually. |
| ch3 | 230VAC external LED lights | Used |  |
| ch4 | Window winch — direction open | Used | Must energise simultaneously with ch6. Never energise with ch5 simultaneously. |
| ch5 | Window winch — direction close | Used | Must energise simultaneously with ch6. Never energise with ch4 simultaneously. |
| ch6 | Window winch — power | Used | Energise simultaneously with ch4 or ch5 only. Never ON without exactly one direction relay. |
| ch7 | 230VAC vacuum pump | Used |  |
| ch8 | Spare | Spare | Available for future use |

## 5.2 W — 15VDC Relay Board (8-channel)

| Channel | Load | Status | Notes |
| --- | --- | --- | --- |
| ch1 | UFH cold valve — direction relay (SPDT) | Used | COM to valve. NO = Wire A (open, +15V). NC = Wire B (close, +15V). GND permanent. Auto-cutout at end stop. No power relay needed. |
| ch2 | Spare | Spare | Previously UFH cold power relay — removed. Auto-cutout eliminates need for power relay. |
| ch3 | Solar cold valve — direction relay (SPDT) | Used | COM to valve. NO = Wire A (open, +15V). NC = Wire B (close, +15V). GND permanent. Auto-cutout at end stop. |
| ch4 | Spare | Spare | Previously solar cold power relay — removed. Auto-cutout eliminates need for power relay. |
| ch5 | Fan flap 15VDC actuator | Used |  |
| ch6 | Door lock relay 1 | Used | H-bridge pair with ch8. Pulse 1s to unlock. |
| ch7 | 15VDC alarm sounder | Used | 1 min auto-stop on intrusion |
| ch8 | Door lock relay 2 | Used | H-bridge pair with ch6 |

## 5.3 W — 4-channel Relay Board (overflow)

| Channel | Load | Status | Notes |
| --- | --- | --- | --- |
| ch1 | Vacuum isolation valve — OPEN | Used | H-bridge pair with ch2 |
| ch2 | Vacuum isolation valve — CLOSE | Used | H-bridge pair with ch1 |
| ch3 | Buzzer signal to H (2.5mm T&E earth) | Used | W relay pulls earth wire to trigger buzzer at H |
| ch4 | Spare | Spare | Available for future use |

## 5.4 H — 15VDC Relay Board (8-channel)

| Channel | Load | Status | Notes |
| --- | --- | --- | --- |
| ch1 | Log burner cold valve — OPEN | Used | H-bridge pair with ch2 |
| ch2 | Log burner cold valve — CLOSE | Used | H-bridge pair with ch1 |
| ch3 | Bottom-of-tank valve — OPEN | Used | H-bridge pair with ch4 |
| ch4 | Bottom-of-tank valve — CLOSE | Used | H-bridge pair with ch3 |
| ch5 | 2-port valve — OPEN (heater side) | Used | H-bridge pair with ch6. COM to valve terminal A. |
| ch6 | 2-port valve — CLOSE (mid-tank side) | Used | H-bridge pair with ch5. COM to valve terminal B. |
| ch7 | 12VDC backup PSU relay | Used | Energise below 12V, de-energise above 12.5V |
| ch8 | Spare | Spare | Previously boost LED — removed from design. Available for future use. |

# 6. Recommended Software Libraries (PlatformIO / Arduino)

| Library | Function | PlatformIO ID |
| --- | --- | --- |
| OneWire + DallasTemperature | DS18B20 1-Wire sensors | paulstoffregen/OneWire + milesburton/DallasTemperature |
| Adafruit INA219 | Solar pump current sensing | adafruit/Adafruit INA219 |
| MCUFRIEND_kbv | ILI9488 3.5″ TFT display | prenticedavid/MCUFRIEND_kbv |
| Adafruit GFX | Graphics primitives for TFT | adafruit/Adafruit GFX Library |
| SD | SD card read/write | arduino-libraries/SD |
| ModbusMaster | Growatt RS485 Modbus RTU | 4-20ma/ModbusMaster |
| ArduinoRS485 | Inter-controller RS485 link | arduino-libraries/ArduinoRS485 |
| RTClib | DS3231 RTC — timestamps and 5am trigger | adafruit/RTClib |
| avr/wdt.h | Hardware watchdog timer | Built-in AVR library — no install needed |
| EEPROM.h | EEPROM storage for settings | Built-in Arduino library — no install needed |

# 7. Commissioning Steps

Follow in order before running any control logic.

- Install CH340 driver on development PC. Verify both Megas appear as COM ports in PlatformIO.

- Upload DS18B20 address-scan sketch to each Mega. Record 64-bit address of every sensor and map to physical location. Update firmware constants.

- Test each relay channel in isolation with multimeter before connecting any loads. Verify NC/NO orientation and flyback diode presence.

- Test each valve H-bridge: energise open relay, confirm valve opens; de-energise, energise close relay, confirm closes. Verify 200ms dead-time interlock.

- Verify RS485 inter-controller link: send test packets from W, confirm receipt at H over full 40m run. Check for framing errors.

- Verify RS485 line bias: confirm stable idle state on A and B lines with no active driver.

- Verify Growatt Modbus: confirm all register readings match Growatt app values. Verify export/import sign convention. Verify 850ms poll rate causes no errors.

- Calibrate voltage divider at H: measure actual 15VDC bus voltage with multimeter, compare to ADC-calculated value. Apply correction factor in firmware.

- Calibrate INA219: run solar pump at known duty cycles, record current draw. Set minimum-current fault threshold at 20% below lowest normal reading.

- Test zero-crossing detector at H: confirm interrupt fires at 50Hz. Simulate grid outage (disconnect AC feed) and verify Mega detects within 50ms.

- Test all safety fault conditions with simulated inputs before connecting heating loads.

- Test DS3231 RTC: set time, remove power for 30 minutes, restore power and confirm time retained correctly.

- Run full system in monitoring-only mode (no actuator outputs) for 24h. Verify SD card logging is complete and consistent.

- Verify watchdog timer: introduce deliberate hang in test firmware, confirm Mega resets within 8 seconds.

# 8. Electrical Safety Notes

- ⚠ All 230VAC wiring must be installed and verified by a competent person. Incorrect mains wiring is a fire and electrocution risk.

- ⚠ Ensure all 230VAC relay outputs are correctly fused. Relay boards typically rated 10A per channel — verify before use.

- ⚠ SSR-40DA carries up to 12.5A. Use 4mm² cable on heater circuit, rated fuse, and ensure heatsink is mounted externally and is adequate.

- ⚠ Never work on 230VAC wiring with mains supply live.

- ⚠ Confirm SSR is zero-crossing type before installation.

- All low-voltage (5V, 15VDC) wiring neatly routed and separated from 230VAC wiring inside enclosures

- Label all terminals clearly on installation

- Ferrite cores on RS485 cables at each end to suppress interference from nearby 230VAC cables

- Verify relay boards include flyback suppression diodes. Add 1N4007 across each relay coil if not present.

# 9. Outstanding / To Be Determined

| Item | Notes |
| --- | --- |
| UFH cold / solar cold valve end-stop | Verify end-stop protection during commissioning before relying on it |
| PC fan minimum PWM duty cycle | Determine minimum duty cycle before fan stalls during commissioning |
| Solar pump minimum current threshold | Calibrate during commissioning |
| Summer mode solar pump minimum speed | Calibrate by on-site testing |
| Growatt register addresses | Verify all register addresses during commissioning |
| RS485 bias resistors | Check if MAX485 boards include internal bias before adding external |
| 12VDC backup PSU specification | Select and specify PSU rated for full load at H |
| Relay board flyback diodes | Verify presence during commissioning before connecting loads |
| Enclosure size confirmation | Confirm 200×150×80mm is sufficient for Mega + relay board + modules |

# 10. Document Changelog

| Version | Changes |
| --- | --- |
| 1.0 | Initial hardware specification |
| 2.5 | W DS18B20 count 5→6: UFH pipe renamed to UFH supply (at pump, 28°C pump-off) and UFH post TMV added (after TMV, 45°C lockout); total DS18B20 count 11→12; BOM updated to 12 sensors; architecture overview, 1-Wire section, and pin assignments updated; sensor fault behaviour documented in requirements spec |