H & W Integrated Control System

Complete Project Reference

Version 5.0  —  Requirements Specification

# 1. Project Status

Requirements gathering complete. Hardware specification complete. Software implementation is the next stage.

# 2. Physical Infrastructure

## 2.1 Cable Runs Between H and W (40m)

- 6mm T&E: Mains power in both directions (grid feed to W from H, PV export from W back to H)

- 2.5mm T&E: Live + Neutral carry 15VDC power to both mid-point momentary switches (unlock and outside light). Earth wire carries buzzer trigger signal from W relay to buzzer at H.

- 1mm T&E cable 1: Live = unlock switch output signal to W / holds LED high when W is unlocked; Neutral = outside light switch output signal to W; Earth = spare

- 1mm T&E cable 2: Both conductors and earth fully spare — intended for inter-controller RS485 communication between H and W controllers

- RS485 screened 24AWG cable: Carries SDM230 meter data to Growatt inverter only. SDM230 physically at W; read by Growatt to calculate grid export

- 4 × 15mm pipes in vacuum-insulated outer pipe: Hot heating system pipe, cold heating system pipe, DHW pipe (future), cold fresh water pipe

- 10mm earth cable: Earthing between H and W

## 2.2 Pipe Bundle Detail

- The vacuum-insulated outer pipe maintains thermal insulation of the 4 inner pipes

- Vacuum pump at W runs to maintain this vacuum whenever the heating system is actively transferring heat in either direction

# 3. Locations & Layout

| Location | Description |
| --- | --- |
| H | The house/dwelling — contains heat store tank, log burner, electric heater, and associated valves and controls |
| W | The workshop — contains solar thermal array, PV inverter, UFH, and associated valves and controls. 40m from H |
| Mid-point | Near the back door of the dwelling. Contains: unlock button, outside light switch, and unlocked LED indicator. Treated as a separate node from H in system topology |

# 4. Components & Sensors

## 4.1 At W (Workshop)

### Heating

- Thermal solar array: 2 × 30 evacuated tubes by Navitron, rated 3.6kW, south-facing wall

- 12VDC brushless pump, under 10W, 2-wire, on cold side of thermal solar. Speed controlled by MOSFET switching 15VDC supply at clocking rate — no separate PWM signal wire

- 2 × 12VDC motorised valves on cold heating system pipe (2-wire, reverse voltage to close): one feeds UFH cold side, one feeds solar cold side via flap non-return valve

- 230VAC central heating pump with thermostatic mixing valve (TMV) for UFH

### PV

- 2 × 3.6kW PV panel strings on flat roof, 10 degree slope, east/west facing

- Growatt SPH6000TL BL-UP inverter

- Growatt GBLI6532 battery

- SDM230 meter (used by Growatt to calculate grid export, read via RS485)

- PV, battery, and grid data available via Growatt Modbus RS485

### Sensors

- DS18B20: solar hot side

- DS18B20: solar cold side

- DS18B20: UFH supply (at UFH pump — return from UFH circuit. Used for logging and pump-off check at 28°C)

- DS18B20: UFH post TMV (after thermostatic mixing valve — supply to UFH pipes. Used for 45°C hard lockout only)

- DS18B20: Workshop air temperature

- DS18B20: outside air temperature

- PIR sensor: 15VDC output when activated — voltage divider required

- Summer/winter mode — REMOVED: now controlled via display at H

- Door reed switch: dry contact, normally open, closes when door opens (opens when door closed)

- Door handle reed switch: dry contact, closed when handle is pushed down

- Window winch reed switches: fully open, fully closed, manual lock

- Window winch safety limit switch: dry contact, normally open, closes at mechanical over-open limit

- Vacuum sensor: dry contact — normally open (HIGH via pull-up = low vacuum), closes when full vacuum achieved (LOW = full vacuum)

- INA219 current sensor module (I2C) on solar pump positive feed

- AC zero-crossing detector module at H (not W) — see H components

### Other

- Electric door lock (15VDC) — 2 relay H-bridge required, pulsed 1s to unlock then de-energised

- 230VAC wall axial fan (S&P HCBB/4-450/H, 480W) with BES fan speed controller (manual dial) and external flap actuator (15VDC)

- 230VAC window winch

- 230VAC vacuum pump with 15VDC motorised isolation valve (2-wire, reverse voltage to close, 2 relays required)

- 230VAC external LED lights

- 15VDC alarm sounder (sounds when PIR detects intruder whilst W is locked, auto-stops after 1 minute)

- Manual latching switch at W — suppresses auto-relock whilst ON

- 2 × Fractal Design Dynamic X2 GP-14 (140mm, 3-pin, 12VDC). MOSFET (IRLZ44N) switches 12VDC supply at 25kHz PWM. Powered from 12V DC-DC buck converter from 15V bus. Momentary push button at W sets 8-hour full speed timer.

## 4.2 At H (House)

### Heating

- 1000L heat store tank with bottom, middle and top pipe connections

- 3kW electric heater: cold side fed by 2-port valve from hot heating pipe from W; output connects to shared manifold with top of tank and log burner hot pipe

- Log burner with 70L water jacket

- 12VDC motorised valve on log burner cold pipe (2-wire, reverse voltage to close, 2 relays)

- 12VDC motorised valve on bottom-of-tank pipe (2-wire, reverse voltage to close, 2 relays)

- 2-port 12VDC motorised valve on hot heating system pipe from W (2-wire, reverse voltage to close, 2 relays): switches between → electric heater cold side OR → middle of tank

- SSR-40DA zero-crossing solid state relay for heater power control (cycle-burst method)

- AC zero-crossing detector module wired to H Mega INT0 pin — serves three functions: (1) cycle-level heater burst timing, (2) instant grid outage detection, (3) grid restore detection

### Sensors

- DS18B20: tank bottom

- DS18B20: tank middle

- DS18B20: tank top

- DS18B20: hot heating system pipe to W

- DS18B20: cold heating system pipe to W

- DS18B20: heater hot side output

- 12VDC temperature module: outputs 12VDC when log burner water jacket exceeds 28°C — voltage divider required

- 15VDC bus voltage monitor: resistor divider (10kΩ + 4.7kΩ) on H Mega ADC pin

### Controls & Indicators

- 3 × panel-mount buttons at H display: SELECT, ▲ (UP), ▼ (DOWN)

- 3.5″ ILI9488 TFT display 480×320 SPI — see Section 9 for full display specification

- MicroSD card module (SPI) for data logging

- DS3231 RTC module (I2C) — essential for 5am heating trigger and time-gated security alerts

- 12VDC backup PSU relay — switched by H Mega when bus voltage drops below 12V

## 4.3 At Mid-Point

- Momentary unlock button (15VDC from 2.5mm T&E live, output on 1mm cable 1 live)

- Momentary outside light switch (15VDC from 2.5mm T&E live, output on 1mm cable 1 neutral)

- LED indicator: controlled entirely by W Mega on D34. Priority order (highest first): (1) Fault active — 1s on / 1s off continuous flash; (2) Manual heater active (no fault) — 1s on / 5s off slow single flash; (3) Workshop unlocked, no fault, no manual heater — steady HIGH; (4) Workshop locked, no fault, no manual heater — off. LED clears to next priority state when higher priority clears.

# 5. Pipe & Valve Topology

## 5.1 Cold Heating System Pipe (H to W)

Feeds from H: log burner cold valve OR bottom-of-tank valve (both connect to same cold pipe). At W: splits to → UFH cold side valve OR solar cold side valve (via non-return flap valve).

## 5.2 Hot Heating System Pipe (W to H)

From W: UFH hot output and solar hot output. At H: enters 2-port valve → switches to heater cold side OR middle of tank. Heater output joins shared manifold → top of tank + log burner hot pipe.

# 6. Security & Access Logic

## 6.1 Door Lock & Unlock

- W door locked by default (15VDC electric lock, 2-relay H-bridge, pulsed 1s to unlock then de-energised)

- Unlock: pressing momentary button at mid-point sends signal to W Mega → door lock pulsed 1s → 1mm T&E live held HIGH → LED at mid-point lights steady

- Door reed switch: dry contact, normally open, closes when door opens, opens when door closes

## 6.2 Auto-Relock Logic

Auto-relock is prevented while ANY of the following conditions are true:

- Door is open (reed switch closed)

- PIR is detecting presence (active output)

- Manual suppression switch at W is ON

- Window is not fully closed AND locked (fully closed reed switch not active OR manual lock reed switch not active)

Relock timer: starts only when ALL four conditions are simultaneously clear. If any condition becomes active during the 5-minute countdown, timer resets to zero. After 5 continuous minutes of all four conditions clear → door relocks.

Log entries: 'Auto-relock prevented — door open', 'Auto-relock prevented — PIR active', 'Auto-relock prevented — suppression switch on', 'Auto-relock prevented — window not closed/locked'

## 6.3 Security Alerts

- Intruder alert: PIR detects movement whilst W is locked → alarm at W sounds for 1 minute then auto-stops; buzzer at H sounds while PIR is active; logged

- Door handle alert: door handle reed switch closes whilst W is locked → between 23:00–06:00 buzzer sounds minimum 10s (continues while held if longer); between 06:00–23:00 buzzer sounds only while handle held; logged with timestamp in both cases

# 7. Lighting & Ventilation Logic

## 7.1 External Lights at W

- Controlled by: momentary switch at mid-point OR momentary switch at W

- 230VAC LED external lights switched by relay

## 7.2 Workshop Fan (S&P HCBB/4-450/H)

- 230VAC axial fan with BES manual speed controller (dial-set speed) and external flap actuator (15VDC)

- Fan on/off controlled by relay on W 230VAC relay board

- Automatic night cooling (230VAC fan only — PC fans are unaffected by night cooling logic): fan ON when outside air is more than 5°C below Workshop air temp; fan OFF when gap closes to 2°C or less

- Night Cooling can be disabled via display toggle at H (page 4). State shown in status bar.

- Flap actuator opens before fan relay energises; closes after fan relay de-energises

## 7.3 Window Winch

- Manual trigger only — 3 relays on W 230VAC relay board (direction open, direction close, power)

Valid relay states — firmware treats as atomic group only:

| State | Relay 1 (direction open) | Relay 2 (direction close) | Relay 3 (power) | Notes |
| --- | --- | --- | --- | --- |
| STOP | OFF | OFF | OFF | Only safe stop state. Power-up default. |
| OPEN | ON | OFF | ON | Relay 1 and 3 energised simultaneously |
| CLOSE | OFF | ON | ON | Relay 2 and 3 energised simultaneously |
| FORBIDDEN | ON | ON | any | Hard interlock — must never occur |
| FORBIDDEN | OFF | OFF | ON | Hard interlock — power without direction |
| FORBIDDEN | ON | OFF | OFF | Hard interlock — direction without power |
| FORBIDDEN | OFF | ON | OFF | Hard interlock — direction without power |

- Direction change: always STOP (all three OFF) → 1 second pause → new direction

- Firmware implementation: single function setWinch(STOP/OPEN/CLOSE) — never set individual relays independently

Immediate stop triggers — de-energise all three relays instantly then apply lockout:

- Fully open reed switch activates → STOP + lock out OPEN direction. Lockout clears when switch deactivates.

- Fully closed reed switch activates → STOP + lock out CLOSE direction. Lockout clears when switch deactivates.

- Manual lock reed switch activates → STOP + lock out BOTH directions. Lockout clears when switch deactivates.

- Safety limit switch activates → STOP + lock out OPEN direction + flash LED + log 'Window Winch Over Open'. Close direction still available. Clears when switch opens.

## 7.4 PC Cooling Fans at W (Fractal Design Dynamic X2 GP-14)

- 2 × 140mm 3-pin 12VDC fans. MOSFET (IRLZ44N) switches 12VDC supply at 25kHz PWM. Powered from 12V DC-DC buck converter from 15V bus.

Fan control modes — priority order:

| Priority | Mode | Speed | Trigger / Duration |
| --- | --- | --- | --- |
| 1 | Full speed timer | 100% | W button press = 8hrs. Adjustable at H display in 1-hour increments (0–24hrs). Counts down regardless of lock status. |
| 2 | Base speed timer | Base % | Set at H display in 1-day increments (0–30 days). Counts down continuously regardless of lock status. When expires → fans off until workshop unlocked. |
| 3 | Workshop unlocked | Base % | Fans run at base speed whenever workshop is unlocked. Off when locked. |
| 4 | Off | 0% | Workshop locked, no timers active. |

- If full speed timer and base speed timer both active: full speed until full speed timer expires → base speed until base speed timer expires → off until unlocked

- Base speed: set at H display in 10% increments (0–100%). Firmware enforces minimum speed if fan stall detected at low duty cycle.

- Tachometer fault: if either fan reads zero RPM when commanded above minimum speed for >5s → flash LED, log fault. No buzzer.

- Status bar on all display pages: 'FAN FULL 07:23' / 'FAN BASE 3d 14h' / 'FAN BASE' / 'FAN OFF'

# 8. Heating Control Logic

## 8.1 Winter Mode

Active when Mode is set to Winter via display at H. UFH heating operates normally.

### Thermal Solar — Winter

- Solar sequence triggers when solar hot side ≥ 18°C

- Open UFH cold valve, open solar cold valve, start solar pump clocking 200ms ON every 2s

- Solar pump speed ramps up starting 2°C below target, reaching 100% at 2°C above target. Winter solar target: 20°C (UFH circuit temperature)

- Fault condition: pump running above clocking speed for >10s AND solar cold side >10°C above tank bottom temperature → thermal solar overheat alert (see Section 11). If tank bottom reading is stale due to RS485 comms fault: do not trigger this fault — assume solar is operating normally.

- When solar hot side is no longer >2°C warmer than cold side: close solar cold valve, stop pump

- Frost protection: if either solar side drops below 2°C → open UFH valve, run solar pump at full speed until solar output reaches 8°C → stop pump but leave UFH valve open until next heating cycle begins or solar reaches 18°C. Runs regardless of heating lockout state.

### Morning Heating Cycle (5am daily, RTC-triggered)

- Trigger: RTC reaches 05:00. No catch-up on power-cut restart — wait for next 5am.

- Normal mode: if W air temp < 13.5°C → open UFH valve + start W central heating pump. Heating stops when W air temp reaches 13.5°C. Once target reached, UFH locked out until next 5am regardless of temperature drop.

- Boost at 5am mode: heating triggers at boost target temp (13–20°C, default 15.5°C), turns OFF at boost target +0.5°C. Active until 10am the following day.

- 8hr boost mode: heating starts immediately regardless of time, runs at boost target temp for 8 hours. UFH lockout still applies once target reached.

- Frost protection during heating: if solar cold side < 2°C → open solar cold valve, run solar pump at full speed until 8°C reached. Runs regardless of heating lockout state.

- UFH overheat: if UFH post TMV temp exceeds 45°C while UFH pump is running → stop pump, close UFH valve, flash LED, log 'UFH Overheat', hard lockout (does not restart until system restart). Frost protection may still use UFH regardless of this lockout.

- Once W air temp reaches target: open log burner cold valve + ensure top-of-tank path is open, close bottom-of-tank valve. W UFH pump continues running until UFH supply thermistor drops below 28°C → everything stops until 5am next day.

### Heat Source Selection at H (when morning heating is ON)

- If log burner temp module active (jacket > 28°C, hysteresis off below 25°C): open log burner cold valve; set 2-port valve to heater cold side (circulates heat from log burner through manifold to top of tank)

- If log burner temp module NOT active: close log burner cold valve, open bottom-of-tank valve

- If middle-of-tank temp > 30°C: switch 2-port valve to middle of tank

- If middle-of-tank temp < 30°C: switch 2-port valve to heater cold side (connects to top of tank via heater)

- Log burner and solar thermal can run simultaneously in winter — both circulate through UFH circuit. This is a valid and expected state requiring no special handling.

### PV Export Override (winter day)

- If PV export reaches 0.5kW during winter mode: switch entirely to summer mode logic (including heater activation). Summer mode continues until PV production drops to zero, then revert to winter mode.

## 8.2 Summer Mode

Active when Mode is set to Summer via display at H, OR when PV export override is active. UFH is completely disabled in summer mode.

### Summer Startup Sequence

Triggered when: PV export reaches 0.5kW OR solar hot side OR solar cold side reaches 50°C.

- Open log burner cold valve + 2-port valve to top-of-tank path → solar pump starts clocking minimum speed → circulate until hot heating pipe reaches bottom-of-tank temperature

- Close log burner cold valve, open bottom-of-tank valve → circulate until hot heating pipe reaches top-of-tank temperature OR electric heater becomes powered

- Once hot pipe matches top-of-tank temperature: switch 2-port valve to heater cold side (water circulates through heater to top-of-tank manifold)

If both triggers fire simultaneously: sequence runs once only (double-start prevention flag). If solar triggers but PV export not yet at 0.5kW: valve startup sequence runs, heater activation waits for export threshold.

### Thermal Solar — Summer

- Solar pump clocks 500ms ON every 20s at minimum speed once summer startup triggered

- Solar pump speed controlled by whichever sensor is closest to or exceeding its target:

- Solar hot side: target = top-of-tank temp + 5°C (Tank+5 mode) OR 80°C max (Max mode). Ramps from 2°C below target to 100% at 2°C above. 80°C absolute maximum prevents overheating.

- Heater output (only when heater powered): target = top-of-tank temp + 5°C (Tank+5 mode) OR 89°C max (Max mode). Pump reaches 100% at 91°C.

- Solar target mode (Tank+5 vs Max) toggled from display page 4. Greyed out in winter mode.

- Solar system stays active while: hot heating pipe is >5°C warmer than cold heating pipe, OR PV panels are producing any power

- When top-of-tank valve held open but heater not powered AND solar temp >15°C below target: solar pump does not clock

- Fault condition: pump running above clocking speed for >10s AND solar cold side >10°C above tank bottom temperature → thermal solar overheat alert (see Section 11). If tank bottom reading is stale due to RS485 comms fault: do not trigger this fault — assume solar is operating normally.

### Electric Heater Control

- Heater powers ON when PV export first reaches 0.5kW (trigger threshold with hysteresis)

- Once running: heater power modulated via SSR cycle-burst to maintain PV export at ~100W

- Heater switches OFF if PV export drops below 0.1kW and cannot be maintained. Must reach 0.5kW again to re-engage.

- Above 91°C heater output: heater power begins reducing

- At 92°C heater output: heater fully off

- When heater stops being powered: 2-port valve remains open (stays connected to heater cold side)

- Once heater no longer powered and solar reaches its own target: top-of-tank valve no longer held open

- Minimum solar pump speed when heater powered: set by heater power level and hot pipe supply temperature — calibration required on-site

### Overheat Protection (summer)

- If heater output >92°C for >1 minute AND heater is off: close bottom-of-tank valve, open log burner cold valve, ensure top-of-tank path open. Hold until solar goes off (PV = zero) → restart from beginning of summer sequence.

## 8.3 Manual Heater Mode

Activated from display page 4. Three states:

| State | Behaviour |
| --- | --- |
| Off | Heater off, no manual control |
| Manual — SOC limited | Heater on, modulated via SSR cycle-burst to keep grid import at ~100W. Auto-off if battery SOC drops to 50%. SOC read from Growatt Modbus. If SOC data older than 10s — force heater off. |
| Manual — override SOC | Full 3kW continuous — SSR held fully ON every cycle. No SOC check, no modulation. Runs until manually cancelled. Display shows red 'MANUAL HTR — FULL 3kW' warning. |

- All heater safety limits apply in all manual states: overheat (91°C), element fail, zero-crossing SSR control

- Grid outage forces heater off in all manual states

- Manual heater state is NOT stored in EEPROM — resets to Off on power cycle

- Logs: 'Manual heater on — SOC limited', 'Manual heater on — SOC override', 'Manual heater off', 'Manual heater auto-off — SOC limit reached'

## 8.4 Solar Pump Speed — General Rules

- Speed ramps linearly: 0% at 2°C below target, 100% at 2°C above target

- In winter: target is W UFH temperature (20°C)

- In summer: target is the lower of the two sensor targets (solar hot side or heater output when powered)

- Minimum pump speed in summer when heater powered: set by heater power level and hot pipe supply temperature — to be calibrated by on-site testing

- Pump controlled by MOSFET (IRLZ44N) switching 15VDC supply at clocking rate. Minimum ON pulse 200ms ensures pump spins reliably.

- INA219 current sampled during ON period only, after 50ms spin-up delay, to avoid false zero readings during OFF periods

# 9. Display Specification

## 9.1 Hardware

- 3.5″ ILI9488 TFT 480×320 SPI display at H

- 3 panel-mount buttons: SELECT, ▲ (UP), ▼ (DOWN)

## 9.2 Button Behaviour

Three navigation modes. SELECT moves one level deeper; scrolling past boundaries then pressing SELECT moves one level back.

| Mode | UP ▲ | DOWN ▼ | SELECT |
| --- | --- | --- | --- |
| Page scroll mode | Previous page | Next page | Enter item mode — highlights first item on current page |
| Item mode — on an item | Move to previous item | Move to next item | Enter option mode for highlighted item |
| Item mode — past top boundary | No action (at boundary) | Move to first item | Exit item mode → return to page scroll mode |
| Item mode — past bottom boundary | Move to last item | No action (at boundary) | Exit item mode → return to page scroll mode |
| Option mode | Previous option / decrement | Next option / increment | Confirm choice → return to item mode |

Visual feedback:

- Current page indicated by page number in status bar

- Highlighted item shown with amber border or inverted background

- Boundary state (past first or last item): highlight clears, subtle exit indicator shown (e.g. '< back to pages >' hint). UP/DOWN still navigates back to items from boundary state.

- Option mode: selected item shows current value cycling with each press

Inactivity and wake:

- 30 seconds no button press in item or option mode → exit to page scroll mode, clear highlight

- 1 hour no button press with no active fault → display backlight turns off

- Any button press wakes display from backlight-off state

- If any fault is active: display stays on, backlight never turns off

- After 1 hour no input: display returns to page 1

Alert reset:

- Physical RESET button removed. Alert reset is an item on page 4 controls — navigate to it with SELECT + UP/DOWN, then press SELECT to acknowledge and clear the flashing LED

- Alert reset item only visible on page 4 when a fault alert is active

- If fault condition still present when reset selected: LED re-triggers immediately

Boost shortcut:

- Double-press SELECT from page scroll mode (not item mode) → toggles Boost at 5am on/off from any page

## 9.3 Persistent Elements (all pages)

- Top status bar: Mode (Winter/Summer), Boost status + countdown, Night Cooling on/off, Solar Target mode (Tank+5/Max), Clock (from RTC)

- Bottom fault bar: all active faults shown with elapsed time. Scrolls if multiple active. Grid Outage shown here, not in status bar.

- Manual override active: red 'MANUAL OVERRIDE ACTIVE — automatic valve control suspended' banner below status bar on all pages

- Manual heater — SOC limited: amber 'MANUAL HEATER — SOC limited' banner below status bar on all pages while active

- Manual heater — Override SOC: red 'MANUAL HEATER — FULL 3kW — no SOC limit' banner below status bar on all pages while active

- If both manual heater and manual valve override are active simultaneously: both banners stack below status bar

## 9.4 Page 1 — Heating System

- Solar / Workshop temperatures: solar hot, solar cold, UFH supply, UFH post TMV, Workshop air, outside air

- Tank / House temperatures: tank top, tank middle, tank bottom, hot pipe, cold pipe, heater output

- Power: heater kW, solar pump %

- Boost panel (when active): Workshop target temp

- Valve states overview: all 6 valves shown as open/closed badges

- Window winch state: open / closed / opening / closing / manual lock / over-open fault

## 9.5 Page 2 — Power & Inverter

- PV: string 1 kW, string 2 kW, total PV kW, today's generation kWh

- Grid: import/export kW with direction indicator (+/−), load power kW, grid voltage V, grid frequency Hz

- Battery: SOC %, charge/discharge power kW (with direction), battery voltage V

- Inverter: status (normal/fault/EPS/standby), temperature °C, fault code if active

- 15V bus voltage V

Note: all data sourced from Growatt Modbus at 850ms poll interval.

## 9.6 Page 3 — Fault History

- Shows all faults logged since last system restart, most recent first

- Each entry shows: fault name, time first occurred, time resolved, duration

- Active faults shown in red. Resolved faults shown in grey.

- Active faults show elapsed time since onset, updating live

- Resolved faults show total duration (resolved time minus onset time)

- If no faults since restart: shows 'No faults recorded since restart'

- Scrollable list — UP/DOWN buttons scroll entries when on this page and no item is highlighted

- Fault data held in RAM — built in memory as faults occur and resolve. Clears on power cycle.

- Maximum ~200 entries before RAM pressure on ATmega2560 (8KB RAM, ~40 bytes per entry). Sufficient for any normal session.

- UP/DOWN in page scroll mode navigates to next/previous page as normal. Alert reset accessible via page 4 controls item.

## 9.7 Page 4 — System Controls

| Order | Item | UP/DOWN action | Values / notes |
| --- | --- | --- | --- |
| 1 | Boost | Cycles: Off → Boost at 5am → 8hr boost → Off | Default: Off. NOT stored in EEPROM. Double-press SELECT from page scroll mode also toggles Boost at 5am. |
| 2 | Boost target | +/−0.5°C per press | 13°C – 20°C. Default: 15.5°C. NOT stored in EEPROM |
| 3 | Mode | Toggle | Winter ↔ Summer |
| 4 | Manual heater | Cycles: Off → SOC limited → Override SOC → Off | NOT stored in EEPROM |
| 5 | Night Cooling | Toggle | On ↔ Off |
| 6 | Solar Target | Toggle (greyed out in winter) | Tank+5°C ↔ Max |
| 7 | Fan base speed | +/−10% per press | 0–100%. Firmware enforces minimum if stall detected. |
| 8 | Fan full speed timer | +/−1 hour per press | 0–24hrs. W button sets 8hrs directly. 0 = cancel timer. |
| 9 | Fan base speed timer | +/−1 day per press | 0–30 days. Counts down regardless of lock status. 0 = off. |
| 10 | Display brightness | +/−10% per press | 10–100% |
| 11 | SD safe remove | SELECT to eject | Flushes writes, closes filesystem. Auto-reinitialises on card reinsert. |
| 12 | Alert reset | SELECT to acknowledge | Only visible when a fault alert is active. Clears flashing LED. Re-triggers immediately if fault still present. |

EEPROM storage: Mode, Night Cooling, Solar Target, Display brightness written after 30s timeout following last change. Boost state, Boost target, Manual heater state NOT stored in EEPROM.

## 9.8 Page 5 — Valve States & Manual Override

- All valve states displayed: UFH cold (Workshop), solar cold (Workshop), vacuum isolation (Workshop), log burner cold (House), bottom-of-tank (House), 2-port (House)

- Window winch status: direction state (idle/opening/closing), reed switch states (fully open, fully closed, manual lock engaged), safety limit switch state

- Manual override entered via SELECT when override item is highlighted. Must be explicitly entered — prevents accidental valve changes.

- In override: UP/DOWN scroll between valves, SELECT toggles valve state, actuates immediately

- Workshop valve override commands sent via RS485 to W Mega for actuation

- Safety faults still function in override — safety always overrides manual state

- Override state NOT stored in EEPROM — always reverts to automatic on power cycle

- Log: 'Manual override entered', 'Manual override exited', with timestamps and valves changed

## 9.9 Page Summary

| Page | Content | Notes |
| --- | --- | --- |
| 1 | Heating system | All temps, heater kW, solar pump %, boost panel, valve overview. Default page on power-on and after 1hr inactivity. |
| 2 | Power & inverter | All Growatt data, PV strings, battery, grid, inverter status, bus voltage |
| 3 | Fault history | All faults since restart, most recent first. Red = active, grey = resolved. |
| 4 | System controls | Boost, mode, manual heater, night cooling, solar target, brightness, SD eject |
| 5 | Valve states & manual override | All valve states. Manual override requires explicit entry. |

# 10. Vacuum System

- Vacuum pump (230VAC) with 15VDC motorised isolation valve (2-wire, reverse voltage to close, 2-relay H-bridge)

- Vacuum sensor: dry contact, normally open (Mega reads HIGH via pull-up = low vacuum), closes when full vacuum achieved (Mega reads LOW)

- System activates when heating or solar becomes active (either direction of heat transfer)

- Sequence: open isolation valve → start vacuum pump → run until vacuum sensor confirms full vacuum (LOW)

- Once full vacuum achieved: run pump for additional 5 minutes, then close isolation valve 10 seconds before pump stops

- Once full vacuum achieved in a session: do not restart pump even if vacuum is subsequently lost. Isolation valve remains closed. Resets at next day's heating/solar activation.

- Maximum runtime: 30 minutes. If full vacuum not achieved within 30 minutes → stop pump, flash LED, log 'Vac Pump Over Runtime'. No buzzer.

# 11. Safety Monitoring & Alerts

Global alert rules:

- Buzzer at H sounds while fault condition is active — stops automatically when condition clears

- Mid-point LED flashes 1s on/1s off from fault onset — continues until Alert Reset is selected on page 4 of H display

- If fault still present when Alert Reset selected: LED re-triggers immediately

- All faults shown on H display fault bar with elapsed time

- All faults logged with timestamp to SD card

- Alert Reset does not affect any heating, pump, or valve states

| Error code | Trigger condition | Actions | Clears / resets |
| --- | --- | --- | --- |
| Thermal Solar Overheat — cold side high | Pump above clocking speed >10s AND solar cold side >10°C above tank bottom | Buzzer + LED flash + Display + Log. If both sides ≤90°C: open UFH valve, close tank valves, remove heater power, run UFH pump + solar pump until clears | Buzzer stops when clears. LED until Alert Reset selected on page 4. |
| Thermal Solar Overheat — hot side high | Tank bottom <70°C AND solar hot >83°C AND pump at 100% | Buzzer + LED flash + Display + Log. UFH dump if both sides ≤90°C | Buzzer stops when clears. LED until Alert Reset selected on page 4. |
| Solar Pump Fault | Pump commanded ON, current below calibrated minimum for >5s | Buzzer + LED flash + Display + Log. UFH dump if both sides ≤90°C | Buzzer stops when clears. LED until Alert Reset selected on page 4. |
| Heater Overheat — power reduction sustained | Heater reducing power due to >91°C output for >20s AND hot pipe <80°C | Log + Display only | Auto-clears when condition resolves. |
| Heater Overheat — heater shut down | Above condition continues >1 minute | Buzzer + LED flash + Display + Log + Heater off | Buzzer stops when clears. LED until Alert Reset selected on page 4. Heater off until restart. |
| Heater Element Fail | Power applied >30s with no temperature rise on heater output | LED flash + Display + Log + Heater off (no buzzer) | LED until Alert Reset selected on page 4. Heater off until system restart. |
| UFH Overheat | UFH post TMV temp >45°C while UFH pump running | LED flash + Display + Log + UFH pump stop + UFH valve close (no buzzer). Hard lockout — does not restart until system restart. Frost protection may still use UFH regardless. | LED until Alert Reset selected on page 4. UFH locked out until restart. |
| Frost Protection — cold side not recovering | Frost protection active >1 min AND solar cold side not yet reached 4°C | LED flash + Display + Log (no buzzer) | LED until Alert Reset selected on page 4. |
| Vac Pump Over Runtime | Vacuum pump running >30 min without achieving full vacuum | LED flash + Display + Log + Pump stopped (no buzzer) | LED until Alert Reset selected on page 4. |
| 15V Bus Low | Bus voltage below 14V for >10s | LED flash + Display + Log (no buzzer) | Clears automatically above 14V. LED until Alert Reset selected on page 4. |
| 12VDC PSU Activated | Bus voltage drops below 12V | Display + Log + 12VDC PSU relay ON | PSU relay off above 12.5V. Logged as '12VDC PSU Deactivated'. |
| 15V Bus Restored | Bus voltage recovers above 14V | Display + Log | LED clears automatically. |
| Grid Outage | Zero-crossing pulses absent >50ms | Display fault bar + Log + Heater forced off (no buzzer, no LED flash) | Auto-clears when grid restored. Logged as 'Grid Restored'. |
| Inverter Fault | Non-zero fault code from Growatt Modbus | LED flash + Display + Log with fault code (no buzzer) | LED until Alert Reset selected on page 4. Clears when fault code returns zero. |
| Growatt Comms Fault | 5+ consecutive failed Modbus polls (~4.25s) | LED flash + Display + Log + Heater forced off (no buzzer) | Clears when comms restore. LED until Alert Reset selected on page 4. |
| Intruder Alert | PIR detects movement whilst W is locked | Buzzer at H (while PIR active) + W alarm 1 min auto-stop + Log | Buzzer stops when PIR clears. No LED flash. |
| Door Handle Alert 23:00–06:00 | Handle reed switch active whilst locked, night hours | Buzzer minimum 10s (continues while held if >10s) + Log | Buzzer stops when handle released (after minimum 10s). |
| Door Handle Alert 06:00–23:00 | Handle reed switch active whilst locked, day hours | Buzzer only while handle held + Log | Buzzer stops immediately on release. |
| Window Winch Over Open | Safety limit switch closes while winch opening | LED flash + Display + Log + Winch open direction locked out (no buzzer) | LED until Alert Reset selected on page 4. Close direction still available. Clears when switch opens. |
| RS485 Comms Fault | 5+ consecutive missed H↔W packets (~1.25s) | LED flash + Display + Log (no buzzer) | Clears when comms resume. LED until Alert Reset selected on page 4. |
| Workshop Fan 1 Fault | Fan 1 tach zero while commanded above minimum speed for >5s | LED flash + Display + Log (no buzzer) | LED until Alert Reset selected on page 4. |
| Workshop Fan 2 Fault | Fan 2 tach zero while commanded above minimum speed for >5s | LED flash + Display + Log (no buzzer) | LED until Alert Reset selected on page 4. |

## 11.2 Sensor Fault Behaviour

DS18B20 fault detection: discard readings of exactly 85.00°C, -127°C, or -128°C. A sensor is considered failed after 3 consecutive invalid readings. Clears when 3 consecutive valid readings received. Log '[sensor] sensor recovered' on recovery.

| Sensor | Action on fault |
| --- | --- |
| Solar hot side | Close log burner cold valve, bottom-of-tank valve, 2-port valve. Open UFH cold valve and solar cold valve. Start UFH pump. Force heater off (must stay off while dump is active). Flash LED. Log 'Solar hot sensor fault — tank valves closed, UFH dump active, heater off'. |
| Solar cold side | Same as solar hot side fault. |
| Heater output | Heater immediately off and locked out until sensor recovers. Flash LED. Log 'Heater output sensor fault — heater locked out'. |
| UFH post TMV | Flash LED + log 'UFH post TMV sensor fault' only. UFH continues but 45°C lockout cannot function — firmware must make this explicit in fault message. |
| UFH supply | Flash LED + log 'UFH supply sensor fault' only. No automatic action. 28°C pump-off check disabled until sensor recovers. |
| Tank top / mid / bot | Flash LED + log '[sensor] sensor fault' only. No automatic action. |
| Hot pipe / cold pipe | Flash LED + log '[sensor] sensor fault' only. No automatic action. |
| Workshop air | Flash LED + log 'Workshop air sensor fault' only. No automatic action. |
| Outside air | Flash LED + log 'Outside air sensor fault' only. No automatic action. |
| Inverter temperature | Flash LED + log 'Inverter temp sensor fault' only. No automatic action. |

# 12. Power Supply & Voltage Management

- System nominal bus voltage: 15VDC (battery-backed)

- Both Mega controllers powered from 15VDC bus via barrel jack (onboard regulator provides 5V and 3.3V)

- Voltage monitoring at H only (not W) via resistor divider (10kΩ + 4.7kΩ) on H Mega ADC pin

| Threshold | Action |
| --- | --- |
| Below 14V for >10s | Flash LED + Log '15V Bus Low'. System keeps running. Buzzer does not sound. |
| Below 12V | Activate 12VDC backup PSU relay at H + Log '12VDC PSU Activated'. PSU powers all loads while bus is below 12.5V. |
| Recovers above 12.5V | Deactivate PSU relay + Log '12VDC PSU Deactivated' |
| Recovers above 14V | Clear LED flash + Log '15V Bus Restored' |

- Grid outage detected instantly via zero-crossing detector at H (≤50ms) — no separate grid voltage monitor needed

- Heater forced off on grid outage regardless of manual mode

# 13. Inter-Controller Communications

- RS485 link over spare 1mm T&E cable between H and W (40m)

- Both MAX485 modules at 9600 baud. Poll interval: 250ms (4 times per second)

- Full cycle time at 9600 baud: Growatt Modbus (~75ms) + W→H packet (~36ms) + H→W packet (~36ms) + processing (~20ms) = ~167ms. Comfortably within 250ms window.

- Growatt Modbus polled at 850ms (manufacturer minimum command period). Separate UART from inter-controller link.

- RS485 line bias resistors: 560Ω pull-up on A line to 5V, 560Ω pull-down on B line to GND at one end of each RS485 run. Verify whether MAX485 boards include these before adding externally.

- If 5 or more consecutive packets missed (~1.25s): RS485 Comms Fault triggered

- On comms failure: W continues on last known H values. H continues on last known W values. Both flag fault.

## 13.1 W → H Packet (every 250ms)

- Solar hot temp, solar cold temp, UFH supply temp, UFH post TMV temp, Workshop air temp, outside air temp

- Solar pump duty %, PV export kW, grid import kW

- Fault flags (all W-side faults)

- Valve states: UFH cold, solar cold, vacuum isolation, door lock, fan flap

- Vacuum pump state, vacuum sensor state

- Door state (open/closed), door lock state (locked/unlocked), PIR state, manual relock switch state

- Window winch state: direction (idle/opening/closing), reed switch states (fully open, fully closed, manual lock), safety limit switch state

- Fan state: current speed %, full speed timer remaining, base speed timer remaining

## 13.2 H → W Packet (every 250ms)

- Tank bottom temp, tank middle temp, tank top temp

- Hot pipe temp, cold pipe temp, heater output temp

- Heater power %, boost status, boost mode (off/5am/8hr), boost target temp

- Mode (winter/summer), night cooling state, solar target mode

- Fan speed command: target duty cycle % (W executes autonomously using this + its own lock state knowledge)

- Actuator override commands: valve states to override at W (from manual override mode on page 5). Includes a command type field to distinguish override commands from normal state data.

- Alert reset acknowledgement

- Time sync (on W request at boot and every hour thereafter)

# 14. Data Logging

- SD card at H only. All W data received via RS485 and logged centrally.

- Continuous log: all 12 DS18B20 temperatures (tank top/mid/bot, hot pipe, cold pipe, heater output, solar hot, solar cold, UFH supply, UFH post TMV, Workshop air, outside air), solar pump %, heater kW, heater restricted flag, PV string 1 & 2, total PV, import/export, load, battery SOC, charge/discharge, battery voltage, grid voltage, grid frequency, inverter temp, inverter status, 15V bus voltage, fan 1 RPM, fan 2 RPM, fan speed % — logged every 250ms

- Event log: all error codes with timestamp, all system state changes (boost on/off, mode change, manual override, grid outage etc.)

- SD card safe remove: page 4 option flushes writes and closes filesystem cleanly before card removal. Auto-reinitialises on card reinsert.

- Log format: CSV for easy import to spreadsheet or analysis tool

# 15. Data Analysis — SD Card & SQLite

## 15.1 Overview

The SD card logs at 250ms intervals producing approximately 345,600 rows per day and ~126 million rows per year — too large for Excel. A SQLite database on a PC provides fast queries across the full dataset with no specialist software required.

## 15.2 Workflow

- Remove SD card from H controller (use SD safe remove option on page 4 first)

- Insert SD card into PC

- Run Python import script — reads CSV and imports into SQLite database file on PC (takes a few minutes for a year of data)

- Run analysis scripts to produce graphs and reports

- Reinsert SD card into H controller (auto-reinitialises)

## 15.3 Planned Analysis Scripts (to be written by Claude Code)

- KWh to heater per day — line/bar graph over 1 year. SQL sums heater power readings per day and converts to kWh.

- Daily temperature graph — for a user-specified date: line graph showing tank bottom/mid/top, solar hot/cold, heating pipe hot/cold, heater output temp. X axis = time, Y axis = 0–100 (degrees °C and pump/heater %). Solar pump % and heater power % also plotted. Heater line shown thicker when power is restricted by temperature (>91°C condition).

- Down-sampling: full 250ms resolution stored on SD card, but daily graphs display 1-minute averages (1,440 points per day) for performance.

- Fault history report — query all fault events, durations, and frequency from database. Useful for identifying recurring faults or patterns.

- Additional analysis scripts to be added as requirements emerge.

## 15.4 Database Schema (guidance for Claude Code)

- Table: readings — timestamp (Unix ms), solar_hot, solar_cold, ufh_pipe, w_air, outside_air, tank_top, tank_mid, tank_bot, hot_pipe, cold_pipe, heater_out, solar_pump_pct, heater_kw, heater_restricted (boolean), pv_string1_kw, pv_string2_kw, pv_export_kw, grid_import_kw, battery_soc_pct, battery_kw, grid_voltage, inverter_temp, bus_voltage_v

- Table: faults — fault_code (text), onset_timestamp, resolved_timestamp (null if still active), duration_seconds

- Table: events — timestamp, event_type, detail (for state changes: boost on/off, mode change, manual override etc.)

- Index on timestamp column in readings table for fast date range queries

# 16. Firmware Notes for Claude Code

- Platform: Arduino C++ on Elegoo Mega 2560 (ATmega2560), PlatformIO build system

- Watchdog timer: enable hardware watchdog on both Megas. If main loop hangs >8s, processor resets automatically. Essential for unattended operation.

- EEPROM write endurance: write to EEPROM only after 30s timeout following last button press, not on every change. ATmega2560 EEPROM rated ~100,000 write cycles per address.

- Manual override persistence: NEVER store override state in EEPROM. Always revert to automatic control on power cycle.

- Boost state and target: NOT stored in EEPROM. Reset to Off and default target on power cycle.

- Time sync: W requests time sync from H on first boot and every hour thereafter. H responds with RTC time. W uses this for all time-dependent logic.

- Summer startup double-start prevention: use a 'sequence active or complete' flag. Reset flag when both solar and PV drop to idle.

- Log burner temp module hysteresis: activate at 28°C, deactivate below 25°C to prevent valve chattering.

- PV export sign convention: verify Growatt Modbus register sign convention during commissioning before enabling heater control.

- DS18B20 addressing: each sensor has a unique 64-bit address. Scan and map all sensors to physical locations during commissioning. Store addresses as firmware constants.

- INA219 solar pump current: sample during ON period only, after 50ms spin-up delay. Calibrate minimum current threshold during commissioning with 20% margin below lowest normal reading.

- Heater cycle-burst control: SSR controlled by toggling D27 at H on/off at each zero-crossing interrupt (every 20ms). Outer control loop updates target ON-cycle ratio every 850ms from Growatt Modbus data.

- UFH overheat hard lockout: set a persistent flag on UFH overheat fault. This flag is cleared only on system restart, not by RESET button. Frost protection bypasses this flag unconditionally.

- RS485 comms resilience: if packet missed, continue on last known values. After 5 consecutive misses, trigger RS485 Comms Fault. Clear fault immediately when comms restore.

- Growatt comms resilience: if 5 consecutive Modbus polls fail, trigger Growatt Comms Fault and force heater off. Resume when comms restore.

- Battery SOC validity: if SOC reading is older than 10s while manual heater SOC-limited mode is active, force heater off.

- Display backlight: PWM-dim backlight via Mega PWM pin. Off after 1hr inactivity with no fault. Any button press wakes display. Never turn off if fault active.

- Flyback diodes: confirm relay boards include suppression diodes. If not, add 1N4007 across each relay coil to protect Mega outputs from back-EMF.

- RTC fallback: if RTC coin cell fails but Mega stays powered, use last known RTC time + millis() elapsed to maintain approximate time. Log 'RTC battery low — time approximate'. If Mega loses power and RTC has no backup time, log 'RTC fault — time unknown. Awaiting sync.' and disable time-dependent functions (5am trigger, night handle alert) until valid time received via RS485 from H.

- millis() overflow: Mega millis() counter overflows after ~49 days. Always compare elapsed time using subtraction (unsigned arithmetic): if (millis() - lastTime >= interval) not if (millis() >= lastTime + interval).

- Growatt heater control commissioning flag: implement a firmware constant HEATER_ENABLED (default false). Heater modulation only activates when set true. Allows full system testing with verified Modbus sign convention before enabling heater. Log 'Heater control disabled — commissioning flag' when false.

- Power-up safe state sequence is strictly sequential — each step completes before the next begins. Approximate total time: door lock 1s + H tank valves 7s each ×3 = 21s + vacuum isolation 7s + UFH/solar cold 30s wait = ~60 seconds minimum before heating logic starts. This is acceptable — do not attempt to parallelise.

- Fan speed control: W controls fan speed autonomously using its own lock state (from door lock relay state D29/D39) combined with fan speed settings received from H via RS485. W transmits door lock state to H every 250ms for display.

- Window winch state machine: strict 3-state machine (STOP/OPEN/CLOSE). All transitions through STOP with 1s pause. State and reed switch states transmitted to H every 250ms. Log all state changes with timestamp.

- RS485 packet format: define structured binary packet with header byte, sequence number, payload fields, and CRC checksum. Sequence numbers allow missed packet detection. CRC allows corrupted packet detection. Claude Code to define exact byte layout before implementation.

- Thermal solar cold side overheat: fault only triggers when pump running above clocking speed for more than 10 seconds AND cold side more than 10°C above tank bottom. Does not trigger during startup clocking phase.

- DS18B20 validity checks: discard any reading of exactly 85.00°C (power-loss mid-conversion fault code), -127°C or -128°C (open circuit fault code), or any reading outside a physically plausible range for that sensor's location. These indicate sensor failure or wiring fault.

- DS18B20 calibration: above 85°C accuracy degrades. During commissioning compare sensor readings against a reference thermometer at high temperatures. Apply correction offsets in firmware constants for safety-critical sensors (heater output, solar hot side).

- UFH cold valve and solar cold valve at W use a single direction relay (SPDT). NO = open (Wire A, +15V). NC = close (Wire B, +15V). GND permanently connected. No power relay needed — auto-cutout at end stop. No timed pulse — relay set and left. Valve holds position at end stop with no power drawn after cutout trips.

- PC fan control: MOSFET switches 12VDC supply at 25kHz PWM. Fan base speed stored in EEPROM (written after 30s timeout). Fan timer values NOT stored in EEPROM — reset to zero on power cycle. Firmware enforces minimum duty cycle if tachometer detects stall. Workshop unlocked state received from W via RS485 to determine fan auto-on.

## 16.1 Valve & Lock Wiring — H-Bridge

All 2-wire motorised valves and the door lock use the same H-bridge wiring with 2 SPDT relay channels:

- Relay 1 COM → Device terminal A

- Relay 2 COM → Device terminal B

- Relay 1 NO → +15VDC

- Relay 2 NO → +15VDC

- Relay 1 NC → GND

- Relay 2 NC → GND

| State | Terminal A | Terminal B | Result |
| --- | --- | --- | --- |
| Both relays OFF | GND (via NC) | GND (via NC) | Device holds position. No power drawn. |
| Relay 1 ON, Relay 2 OFF | +15VDC (via NO) | GND (via NC) | Current flows A→B. Valve opens / lock unlocks. |
| Relay 1 OFF, Relay 2 ON | GND (via NC) | +15VDC (via NO) | Current flows B→A. Valve closes / lock locks. |
| Both relays ON | +15VDC | +15VDC | No current flows — harmless but avoid. Use dead-time. |

## 16.2 Valve & Lock Pulse Timings

| Device | Location | Wiring | Control |
| --- | --- | --- | --- |
| Log burner cold valve | H | H-bridge (2 relays) | 7s pulse open or close. Both relays OFF after pulse. Holds position. |
| Bottom-of-tank valve | H | H-bridge (2 relays) | 7s pulse open or close. Both relays OFF after pulse. Holds position. |
| 2-port valve | H | H-bridge (2 relays) | 7s pulse open or close. Both relays OFF after pulse. Holds position. |
| Vacuum isolation valve | W | H-bridge (2 relays) | 7s pulse open or close. Both relays OFF after pulse. Holds position. |
| UFH cold valve | W | Single direction relay (SPDT) | NO = open (Wire A). NC = close (Wire B). GND permanent. Auto-cutout at end stop. No timed pulse. 1 relay only. |
| Solar cold valve | W | Single direction relay (SPDT) | NO = open (Wire A). NC = close (Wire B). GND permanent. Auto-cutout at end stop. No timed pulse. 1 relay only. |
| Door lock | W | H-bridge (2 relays) | 1s pulse to lock, 1s pulse to unlock. Both relays OFF after pulse. Motor-driven, no spring return. |

## 16.3 Valve & Lock Control Rules

- Dead-time: 200ms between de-energising one relay and energising the other. Always apply regardless of direction change.

- Interrupt handling: if a new command arrives before the current pulse has completed, apply 200ms dead-time then start the new command for the full pulse duration. 7 seconds from any intermediate position will always reach the end stop since 7s is the full worst-case travel time.

- Never interrupt a pulse for anything other than a hard safety fault (e.g. UFH overheat, thermal solar overheat).

- After pulse completes: both relays return to OFF. Valve/lock holds position with no power drawn.

## 16.4 Power-Up Safe State Sequence

On every power-up, before any heating logic runs, drive all devices to a defined safe state in this order:

- Door lock → send 1s lock pulse. If door reed switch shows door open: log 'Lock pulse sent — door open' but proceed. Record state as locked.

- All tank valves at H (log burner cold, bottom-of-tank, 2-port) → send 7s close pulse. Wait for completion.

- Vacuum isolation valve at W → send 7s close pulse. Wait for completion.

- UFH cold valve and solar cold valve at W → set direction relay to close, wait 30 seconds (conservative allow for auto-cutout to trip and motor to stop), then leave relay in close position. No current feedback available.

- Window winch → no power-up action. State determined from reed switches.

- Begin normal heating logic only after all devices are in known state.

Rationale: valve and lock positions are unknown after a power cut. Always establishing a known state before starting control logic prevents incorrect valve configurations.

## 16.5 Lock State Tracking

- Lock state tracked in software only — no position feedback from lock mechanism

- On power-up: always send lock pulse regardless of previous state (see power-up sequence above)

- If door reed switch shows door open when lock pulse is due: log anomaly but send pulse and record state as locked

- Lock state NOT stored in EEPROM — power-up always triggers lock pulse

# 17. Growatt SPH6000TL BL-UP Modbus Register Reference

Source documents (fetch directly for Claude Code):

- Protocol V1.20: https://github.com/nygma2004/growatt2mqtt/blob/main/Growatt%20PV%20Inverter%20Modbus%20RS485%20RTU%20Protocol%20v120.pdf

- Protocol V1.24: https://github.com/johanmeijer/grott/blob/master/documentatie/Growatt-Inverter-Modbus-RTU-Protocol-II-V1-24-English-new.pdf

- SPH-specific registers: https://github.com/8none1/growatt_sph_nodered/blob/main/registers.md

SPH register ranges: 03 (holding) 0–124, 1000–1124. 04 (input) 0–124, 1000–1124.

Default baud rate: 9600. Minimum command period: 850ms. Max read: 125 words.

## 17.1 Input Registers (Function 04) — 0–124 range (live inverter data)

| Register | Description | Scale | Notes |
| --- | --- | --- | --- |
| 0 | Inverter status | — | 0=standby, 1=normal, 3=fault, 5=PV+batt online, 6=batt only |
| 3 | PV string 1 voltage (Vpv1) | ×0.1V |  |
| 4 | PV string 1 current (Ipv1) | ×0.1A |  |
| 5–6 | PV string 1 power (Ppv1 H/L) | ×0.1W | 32-bit value across 2 registers |
| 7 | PV string 2 voltage (Vpv2) | ×0.1V |  |
| 8 | PV string 2 current (Ipv2) | ×0.1A |  |
| 9–10 | PV string 2 power (Ppv2 H/L) | ×0.1W | 32-bit |
| 35–36 | Total output power (Pac H/L) | ×0.1W | 32-bit |
| 37 | Grid frequency (Fac) | ×0.01Hz |  |
| 38 | Grid voltage (Vac1) | ×0.1V |  |
| 53–54 | Energy today (Eac_today H/L) | ×0.1kWh | 32-bit. Note: may undercount on hybrid — use PV string registers for accurate daily total |
| 55–56 | Energy total (Eac_total H/L) | ×0.1kWh | 32-bit |

## 17.2 Input Registers (Function 04) — 1000 range (battery & hybrid data)

| Register | Description | Scale | Notes |
| --- | --- | --- | --- |
| 1000 | System work mode | — | 0=waiting, 1=self-test, 3=fault, 5=PV+batt online, 6=batt only |
| 1009–1010 | Battery discharge power (H/L) | ×0.1W | 32-bit. Non-zero when battery is discharging. |
| 1011–1012 | Battery charge power (H/L) | ×0.1W | 32-bit. Non-zero when battery is charging. |
| 1013 | Battery voltage | ×0.1V |  |
| 1014 | Battery SOC | % | Direct percentage. No scaling. ⚠ Verify this is the correct SOC register during commissioning. |
| 1021–1022 | Grid import power (H/L) | ×0.1W | 32-bit. ⚠ Verify sign convention during commissioning before enabling heater. |
| 1023–1024 | Grid export power (H/L) | ×0.1W | 32-bit. ⚠ Verify sign convention during commissioning before enabling heater. |

⚠ Battery charge and discharge are in separate registers — direction determined by which register is non-zero. Grid import and export are also in separate registers. Verify all register addresses and scaling against Protocol V1.20 during commissioning. Enable HEATER_ENABLED flag only after confirming export/import sign convention on your specific unit.

# 19. Outstanding / To Be Determined

| Item | Notes |
| --- | --- |
| UFH cold valve pulse / travel | Power until end stop — no timed pulse. Verify end-stop protection during commissioning. |
| Solar cold valve pulse / travel | Power until end stop — no timed pulse. Verify end-stop protection during commissioning. |
| PC fan minimum PWM duty cycle | Calibrate minimum duty cycle before stall during commissioning. Set as firmware constant. |
| UFH/solar cold valve 30s power-up wait | 30s conservative wait assumed for auto-cutout to trip. Verify during commissioning and adjust firmware constant if needed. |
| Solar pump minimum current threshold | Calibrate during commissioning with 20% margin below lowest normal reading |
| Summer mode solar pump minimum speed | Minimum speed vs heater power level and supply temperature — calibrate by on-site testing |
| Vacuum sensor polarity | Confirmed: dry contact, normally open (HIGH via pull-up = low vacuum), closes = full vacuum. Verify wiring polarity during commissioning. |
| Growatt Modbus register addresses | Verify correct register addresses against protocol document during commissioning. Verify 850ms minimum poll period. Verify export/import sign convention before enabling HEATER_ENABLED flag. |
| RS485 line bias resistors | Check if MAX485 boards include internal bias. Add external 560Ω resistors if not. |
| DHW pipe control | To be added at a later date |
| Auto-relock reliability | Verify all 4 conditions (door, PIR, switch, window) work correctly during installation |
| VFD for workshop fan | Deferred — BES manual speed controller selected instead. |

# 20. Document Changelog

| Version | Changes |
| --- | --- |
| 1.0 | Initial complete requirements specification |
| 2.0–4.0 | Display, alerts, solar, heating refinements |
| 5.0 | Major update: 15VDC, display, valves, fans, RS485, Growatt, all firmware notes |
| 5.1–5.7 | Iterative refinements: fault history, button redesign, valve wiring, fan control, RS485 packets, RTC fallback, pre-coding review |
| 5.8 | UFH sensors: UFH supply (at pump, 28°C pump-off) and UFH post TMV (45°C lockout); W sensors 5→6, total DS18B20 11→12; sensor fault behaviour table (solar=dump+heater off, heater output=heater off, others=LED+log); solar dump forces heater off; relock now 4-condition (adds window not closed/locked); Growatt register reference appendix (section 17); SD card log list confirmed; window relock log entries added |
| 5.9 | Heat source selection: explicit if/else conditions; log burner + solar simultaneous confirmed valid; RS485 fallback for solar cold overheat check (stale tank bottom = no fault); night cooling explicitly 230VAC fan only; power-up sequence timing noted (~60s, strictly sequential) |